## SMA SC146
SMA PPC_C121 | [7 empty] | SMASC_D146
CONs |  |  |  |  | Prev version | Gidginbung |  | CON | Parameter | Description | Range | Default | Prev vesrsion | Gidginbung
CON | Parameter | Description | Range | Default |  |  |  | J | PPrim ♬ | Primary power (irradiation) in p.u. | 0 … 1 | 0.8371 | 1 | 1
J | CtlMod | Controller type selection Power factor control (0) | 0 … 4 | 2 | 3 | 2 |  | J+1 | PWNom ♬ | Maximum active power in p.u.; ig- nored at initialization | 0 … 1 | 0.8371 | 1 | 1
J+1 | KP_PF | Power factor PI controller propor- tional gain | 0 … tbd | 0 | 0 | 0 |  | J+2 | QVArNom ♬ | Reactive power set-point in p.u.; ig- nored at initialization | - sin(acos(PFLim)) … sin(acos(PFLim)) | 0.3117 | 0 | 0
J+2 | KI_PF | Power factor PI controller integral gain | 0 … tbd | 0.5 | 4 | 1 |  | J+3 | PFLim ♬ | Reactive power capability of the de- vice; reactive power is calculated from PFLim by sin(acos(PFLim)) | 0.8 … 1 | 0.8 | 0.9 | 0.9
J+3 | PFXdcrTm | Power factor transducer time delay in s | 0.01 … 100 | 0.03 | 0.04 | 0.03 |  | J+4 | PFPF ♬ | Power factor set-point; ignored at ini- tialization | PFLim … 1 | 0.8356 | 0.9 | 0.9
J+4 | PFDB | Power factor deadband | 0 … 1 | 0 | 0 | 0 |  | J+5 | PFPFExt ♬ | Excitation for power factor control; ig- nored at initialization | 0: overexcited* 1: underexcited* | 0 | 1 | 0
J+5 | KP_Vol | Voltage PI controller proportional gain | 0 … tbd | 0 | 0 | 0 |  | J+6 | QVArMod ♬ | Reactive power mode | 0: Power factor 1: Q set-point 2: Power factor(P) 3: Q(U) | 1 | 1 | 1
J+6 | KI_Vol | Voltage PI controller integral gain | 0 … tbd | 0.5 | 8 | 0.5 | 0.5 | J+7 | QoDEna ♬ | Activation of “Q on Demand” func- tion | 0: deactivated 1: activated | 0 | 0 | 0
J+7 | VolXdcrTm | Voltage transducer time delay in s | 0.01 … 100 | 0.03 | 0.02 | 0.02 |  | J+8 | QoDQMax ♬ | Reative power limit for “Q on De- mand” function | 0 … 1 | 0.3 | 0.3 | 0.3
J+8 | VolDB | Voltage deadband | 0 … 1 | 0 | 0 | 0.01 |  | J+9 | VarCtlVol_Volref ♬ | Reference voltage for Q(U) voltage control in p.u. | 0.8 … 1.2 | 1.0345 | 1 | 1
J+9 | PFNomTot | ` | ±0.8 …1 | 0.9123 | 0 | 0.9123 |  | J+10 | VarCtlVol_VolDB ♬ | Width for symmetric deadband for Q(U) voltage control in p.u. | 0 … 0.2 | 0 | 0.01 | 0.01
J+10 | VolNomTot | Remote bus voltage set-point in p.u. | 0.8 … 1.2 | 1.0123 | 1 | 1 |  | J+11 | VarCtlVol_VarGra ♬ | Gradient for Q(U) statics ∆Q[p.u.]/∆U[p.u.] | 0 … 25 | 5 | 14.066 | 14.066
J+11 | QNomTotHyb | Hybrid control reactive power set- point in p.u. | 0 … 1 | 0 | 0 | 0 |  | J+12 | VarCtlVol_VarMax ♬ | Maximum absolute reactive power for Q(U) in p.u. | 0 … 0.6 | 0.5 | 0.422 | 0.422
J+12 | VolDiff | Voltage droop characteristics: voltage difference in p.u. | 0 … 1 | 0.2 |  | 0.035 |  | J+13 | VarCtlVol_VarTm ♬ | First-order time constant for Q(U) dy- namics in s | 2 … 60 | 2 | 60 | 60
J+13 | HybCtlTun | Hybrid control tuning parameter | 0 … 1 | 0.0268 | 0.0938 | 0.0938 |  | J+14 | PFPFExtStr ♬ | Excitation of the start point for PF(P) control | 0: overexcited* 1: underexcited* | 0 | 0 | 0
J+14 | KP_P | Active power PI controller propor- tional gain | 0 … tbd | 0 | 1 | 0 |  | J+15 | PFPFStr ♬ | Power factor of the start point for PF(P) control | PFLim … 1 | 0.9 | 0.9 | 0.9
J+15 | KI_P | Active power PI controller integral gain | 0 … tbd | 0.5 | 2 | 0.5 |  | J+16 | PFWStr ♬ | Active power of the start point for PF(P) control in p.u. | 0 … 1 | 0.5 | 0.5 | 0.5
J+16 | PXdcrTm | Active/reactive power transducer time delay in s | 0.01 … 100 | 0.03 | 0.04 | 0.03 |  | J+17 | PFPFExtStop ♬ | Excitation of the stop point for PF(P) control | 0: overexcited* 1: underexcited* | 1 | 1 | 1
J+17 | PDB | Active power deadband | 0 … 1 | 0 | 0 | 0 |  | J+18 | PFPFStop ♬ | Power factor of the stop point for PF(P) control | PFLim … 1 | 0.9 | 0.9 | 0.9
J+18 | PNomTot | Plant active power set-point | 0 … 1 | 0.9123 | 0.9 | 0.9 |  | J+19 | PFWStop ♬ | Active power of the stop point for PF(P) control in p.u. | 0 … 1 | 0.9 | 0.9 | 0.9
J+19 | QCommTm | PPC-to-inverter communication time delay for reactive power command in s | 0.01 … 1.0 | 0.04 | 0.2 | 0.04 |  | J+20 | WCtlHzMod ♬ | P(f) droop mode | 0: deactivated 1: activated | 0 | 1 | 0
J+20 | PCommTm | PPC-to-inverter communication time delay for active power command in s | 0.01 … 1.0 | 0.04 | 0.2 | 0.04 |  | J+21 | PHzStr ♬ | Grid frequency offset for starting power reduction in Hz | 0 … 5 | 0.2 | 0.15 | 0.2
J+21 | QSptLimNeg | Negative reactive power set-point EFD(I)) limit in p.u. | 0.0 … -0.6 | -0.6 |  | -0.6 |  | J+22 | PhzStop ♬ | Grid frequency offset for power reset- ting in Hz | 0 … 5 | 0.05 | 0.05 | 0.05
J+22 | QSptLimPos | Positive reactive power set-point EFD(I)) limit in p.u. | 0.0 … 0.6 | 0.6 |  | 0.6 |  | J+23 | PWGra ♬ | Gradient for power reduction in p.u./Hz | 0 … 1 | 0.5 | 0.2 | 0.5
J+23 | FRTThrVolNomMin | Voltage limit for detecting undervolt- age conditions | 0 … 1 | 0.87 | 0.88 | 0.88 |  | J+24 | WGra ♬ | Gradient of changing active power set-point in p.u./s | 0 … 1 | 1 | 0.26 | 0.26
J+24 | Reserved |  |  | 0.87 | 0.88 | 0.88 |  | J+25 | VarGra ♬ | Gradient of changing reactive power set-point in p.u./s | 0 … 2 | 1 | 1 | 1
J+25 | FRTThrVolNomMax | Voltage limit for detecting overvoltage conditions | 1 … 2 | 1.13 | 1.12 | 1.12 |  | J+26 | FRTMod ♬ | Dynamic grid support mode; Note that the “DGS limited” behavior correlates to SC CP firmware release 13 while the “DGS full” behavior cor- relates to all SC types. | 0: “DGS limited“ 1: “DGS full” (“BDEW”) 2: “DGS full” (“SDLWindV”) | 2 | 2 | 2
J+26 | Reserved |  |  | 1.13 | 1.12 | 1.12 |  | J+27 | FRTArGraNom 2♬ | Static reactive current feed-in factor K =∆Ir/∆U (“BDEW curve”) | 0 … 10 | 2 | 2 | 4
J+27 | FRTHldTm | During this time after fault recovery the plant controller model is stopped | 0 … 60 | 0.2 | 0.8 | 0 |  | J+28 | FRTArGraNomHi 2♬ | Static reactive current feed-in factor K =∆Ir/∆U for high voltages (“SDL- WindV” curve) | 0 … 10 | 1.5 | 2 | 2
J+28 | Reserved |  |  | 0.1 | 1 | 0.1 |  | J+29 | FRTArGraNomLo 2♬ | Static reactive current feed-in factor K =∆Ir/∆U for low voltages (“SDL- WindV” curve) | 0 … 10 | 1.5 | 2 | 4
J+29 | KP_Q | Reactive power PI controller propor- tional gain | 0 … tbd | 0 | 0 | 1 | 1.5 | J+30 | FRTDbVolNomMax 3♬ | Positive dead-zone for “DGS full” in p.u. | 0 … 1 | 0.1 | 0.14 | 0.13
J+30 | KI_Q | Reactive power PI controller integral gain | 0 … tbd | 0.5 | 0.5 | 0.5 | 2.5 | J+31 | Reserved |  |  | 0.1 | 0.14 | 0.13
J+31 | QXdcrTm | Reactive/reactive power transducer time delay in s | 0.01 … 100 | 0.03 | 0.04 | 0.03 |  | J+32 | FRTDbVolNomMin 3♬ | Negative dead-zone for “DGS full” in p.u. | 0 … 1 | 0.1 | 0.14 | 0.13
J+32 | QDB | Reactive power deadband | 0 … 1 | 0 | 0 | 0 |  | J+33 | Reserved |  |  | 0.1 | 0.14 | 0.13
J+33 | QNomTot | Plant reactive power set-point | 0 … 1 | 0.123 | 1 | 1 |  | J+34 | FRTWRcvrTmF ♬ | Recovery time constant (first-order de- lay) of active power after dynamic grid support “DGS full” in s | 0.01 … 10 | 0.03 | 0.03 | 0.03
J+34 | PRefTot | Total active power reference of all controlled generators in MVA; If set to zero, MBASE(I) is used |  | 0 | 0 | 0 |  | J+35 | FRTWRcvrTmP | Recovery time constant (first-order de- lay) of active power after dynamic grid support “DGS limited” in s | 0.01 … 10 | 0.05 | 0.02 | 0.05
J+35 | QRefTot | Total reactive power reference of all controlled generators MVA; If set to zero, MBASE(I) is used |  | 0 | 0 | 0 |  | J+36 | VarCmdFltTm ♬ | Reactive current first-order delay block time constant in s; Please set this parameter to 0.01 if you are experiencing problems with oscillations in your simulations. | 0 … 0.1 | 0.01 | 0.01 | 0.01
J+36 | WCtlHzMod | P(f) droop mode; Set to 2 if you want to obtain the fre- quency droop characteristics of the Fuel Save Controller functionality | 0: deactivated 1: activated (2: frequency droop mode) | 0 | 1 | 0 |  | J+37 | FRTPreErrVEna ♬ | Defines DGS pre-error voltage calcu- lation method. If deactivated, the DGS voltage deviation signal is calcu- lated by U/Unom – 1. If activated, the DGS voltage deviation signal is calcu- lated by U/Upre -1, where Upre is the first-order lag low-pass filtered voltage U. | 0: deactivated 1: activated | 0 | 0 | 0
J+37 | PHzStr | Grid frequency offset for starting power reduction in Hz | 0 … 5 | 0.2 | 0.2 | 0.2 |  | J+38 | FRTPreErrTm ♬ | Time constant of first-order lag low- pass filter for pre-error voltage calcu- lation | 0 … tbd | 20 | 0.01 | 0.01
J+38 | PHzStop | Grid frequency offset for power reset- ting in Hz | 0 … 5 | 0.05 | 0.05 | 0.05 |  | J+39 | FRTSwOffTm ♬ | FRT hold time – time for which FRT current characteristics is held after a fault has been cleared (voltage re- turned to deadband). | 0 … 10 | 0.1 | 0.5 | 0.1
J+39 | PWGra | Gradient for power reduction in p.u./Hz | 0 … 1 | 0.5 | 0.4 | 0.4 |  | J+40 | FRTAmpQGra ♬ | Gradient of reactive current filter after FRT exit in p.u. | 0.01 … 100 | 0.1 | 100 | 100
J+40 | HzFltTm | Time constant of first-order lag fre- quency filter; if this parameter is > 0 then the frequency is determined by filtering the system frequency (1.0 + BSFREQ(IB))*f) with this filter, where f = 50 or 60; set to 0 to deactivate | 0 … 1 | 0.01 | 0.01 | 0.01 |  | J+41 | FRTSpkMtgLo ♬ | Lower threshold for FRT spike mitiga- tion; set this parameter so that is it well above the voltage during the fault; see section 4.3.3 | 0 … 1- FRTDb- VolNomMin | 0 | 0.6 | 0
J+41 | WctlHzDrgIndEna | P(f) Drag indicator | 0: deactivated 1: activated | 0 | 0 | 0 |  | J+42 | FRTSpkMtgHi ♬ | Upper threshold for FRT spike mitiga- tion; set slightly higher than FRTSpkMtgLo; see section 4.3.3 | 0 … 1- FRTDb- VolNomMin | 0 | 0.75 | 0
J+42 | PNomTotGraMin | Lower active power set-point ramp rate limit in p.u./s | 0 … tbd | 1 | 1 | 1 |  | J+43 | Reserved |  |  | 0 | 0 | 0
J+43 | PNomTotGraMax | Upper active power set-point ramp rate limit in p.u./s | 0 … tbd | 1 | 1 | 1 |  | J+44 | Reserved |  |  | 0.125 | 0.15 | 0.125
J+44 | FSCFlag | FSC flag (treat ICON(M+4) as PV generator and ICON(M+5)) as bat- tery generator | 0: deactivated 1: activated | 0 | 0 | 0 |  | J+45 | Reserved |  |  | 0.1 | 0.1 | 0.1
J+45 | FD_IPXArr_0 | Frequency droop characteristics x0 | 45 … 65 | 47 | 47 | 47 |  | J+46 | VCtl_Hi5Lim ♬ | Voltage limit for high voltage decou- pling protection (U5>) in p.u. | s. Technical Infor- mation sheet | 1.6 | 1.5 | 1.5
J+46 | FD_IPXArr_1 | Frequency droop characteristics x1 | 45 … 65 | 48 | 48 | 48 |  | J+47 | VCtl_Hi5LimTm ♬ | Delay for high voltage decoupling protection (U5>) in s | s. Technical Infor- mation sheet | 0.01 | 0.01 | 0.01
J+47 | FD_IPXArr_2 | Frequency droop characteristics x2 | 45 … 65 | 49.7 | 49 | 49.7 |  | J+48 | VCtl_Hi4Lim ♬ | Voltage limit for high voltage decou- pling protection (U4>) in p.u. | s. Technical Infor- mation sheet | 1.5 | 1.5 | 1.5
J+48 | FD_IPXArr_3 | Frequency droop characteristics x3 | 45 … 65 | 49.85 | 49.85 | 49.85 |  | J+49 | VCtl_Hi4LimTm ♬ | Delay for high voltage decoupling protection (U4>) in s | s. Technical Infor- mation sheet | 0.01 | 0.01 | 0.01
J+49 | FD_IPXArr_4 | Frequency droop characteristics x4 | 45 … 65 | 50.15 | 50.15 | 50.15 |  | J+50 | VCtl_Hi3Lim ♬ | Voltage limit for high voltage decopling protection (U3>) in p.u. | s. Technical Infor- mation sheet | 1.4 | 1.45 | 1.45
J+50 | FD_IPXArr_5 | Frequency droop characteristics x5 | 45 … 65 | 51 | 51 | 51 |  | J+51 | VCtl_Hi3LimTm ♬ | Delay for high voltage decoupling protection (U3>) in s | s. Technical Infor- mation sheet | 0.01 | 0.5 | 0.5
J+51 | FD_IPXArr_6 | Frequency droop characteristics x6 | 45 … 65 | 52 | 52 | 52 |  | J+52 | VCtl_Hi2Lim ♬ | Voltage limit for high voltage decopling protection (U2>) in p.u. | s. Technical Infor- mation sheet | 1.3 | 1.3 | 1.3
J+52 | FD_IPXArr_7 | Frequency droop characteristics x7 | 45 … 65 | 52.65 | 53 | 52.65 |  | J+53 | VCtl_Hi2LimTm ♬ | Delay for high voltage decoupling protection (U2>) in s | s. Technical Infor- mation sheet | 1 | 1 | 1
J+53 | FD_IPYArr_0 | Frequency droop characteristics y0 | -1 … 1 | 0.05 | 1 | 0.05 |  | J+54 | VCtl_Hi1Lim ♬ | Voltage limit for high voltage decopling protection (U1>) in p.u. | s. Technical Infor- mation sheet | 1.2 | 1.2 | 1.2
J+54 | FD_IPYArr_1 | Frequency droop characteristics y1 | -1 … 1 | 0.05 | 0.8 | 0.05 |  | J+55 | VCtl_Hi1LimTm ♬ | Delay for high voltage decoupling protection (U1>) in s | s. Technical Infor- mation sheet | 3 | 30 | 30
J+55 | FD_IPYArr_2 | Frequency droop characteristics y2 | -1 … 1 | 0.05 | 0.4 | 0.05 |  | J+56 | VCtl_Lo1Lim ♬ | Voltage limit for low voltage decou- pling protection (U1<) in p.u. | s. Technical Infor- mation sheet | 0.8 | 0.85 | 0.85
J+56 | FD_IPYArr_3 | Frequency droop characteristics y3 | -1 … 1 | 0 | 0 | 0 |  | J+57 | VCtl_Lo1LimTm ♬ | Delay for low voltage decoupling pro- tection (U1<) in s | s. Technical Infor- mation sheet | 5 | 30 | 30
J+57 | FD_IPYArr_4 | Frequency droop characteristics y4 | -1 … 1 | 0 | 0 | 0 |  | J+58 | VCtl_Lo2Lim ♬ | Voltage limit for low voltage decou- pling protection (U2<) in p.u. | s. Technical Infor- mation sheet | 0.4 | 0.75 | 0.75
J+58 | FD_IPYArr_5 | Frequency droop characteristics y5 | -1 … 1 | -0.3043 | -0.4 | -0.3043 |  | J+59 | VCtl_Lo2LimTm ♬ | Delay for low voltage decoupling pro- tection (U2<) in s | s. Technical Infor- mation sheet | 2 | 5 | 20
J+59 | FD_IPYArr_6 | Frequency droop characteristics y6 | -1 … 1 | -0.6623 | -0.8 | -0.6623 |  | J+60 | VCtl_Lo3Lim ♬ | Voltage limit for low voltage decou- pling protection (U3<) in p.u. | s. Technical Infor- mation sheet | 0.3 | 0.4 | 0.4
J+60 | FD_IPYArr_7 | Frequency droop characteristics y7 | -1 … 1 | -1 | -1 | -1 |  | J+61 | VCtl_Lo3LimTm ♬ | Delay for low voltage decoupling pro- tection (U3<) in s | s. Technical Infor- mation sheet | 2 | 2 | 2
J+61 | RRCFlag | Enables ramp rate control | 0: deactivated 1: activated | 0 | 0 | 0 |  | J+62 | VCtl_Lo4Lim ♬ | Voltage limit for low voltage decou- pling protection (U4<) in p.u. | s. Technical Infor- mation sheet | 0.2 | 0.3 | 0.3
J+62 | FallRateMax | Lower PV active power ramp rate | 0 … 1 | 0.01 | 1 | 0.01 |  | J+63 | VCtl_Lo4LimTm ♬ | Delay for low voltage decoupling pro- tection (U3<) in s | s. Technical Infor- mation sheet | 2 | 2 | 2
J+63 | RiseRateMax | Lower PV active power ramp rate | 0 … 1 | 0.01 | 1 | 0.01 |  | J+64 | VCtl_Lo5Lim ♬ | Voltage limit for low voltage decou- pling protection (U5<) in p.u. | s. Technical Infor- mation sheet | 0.1 | 0.1 | 0.1
J+64 | PDiffMin | Limit for difference between PV active power and signal PPVRamp | 0 … 1 | 0 | 0 | 0 |  | J+65 | VCtl_Lo5LimTm ♬ | Delay for low voltage decoupling pro- tection (U5<) in s | s. Technical Infor- mation sheet | 2 | 1.5 | 1.5
J+65 | PSuppMax | Maximum battery support active power in RRC mode | 0 … 1 | 1 | 1 | 1 |  | J+66 | HzCtl_Hi6Lim ♬ | Frequency limit for high frequency de- coupling protection (f6>) in Hz | s. Technical Infor- mation sheet | 59 | 55 | 59
J+66 | PPVChargeMax | Maximum battery charge active power in RRC mode | 0 … 1 | 1 | 1 | 1 |  | J+67 | HzCtl_Hi6LimTm ♬ | Delay for high frequency decoupling protection (f6>) in s | s. Technical Infor- mation sheet | 0.01 | 0.05 | 0.01
J+67 | SMASCCONI | Set to zero to suppress writing to file SMASCCONi.txt (needed for multiple generator support, i.e. when ICON(M+4), ICON(M+5), … are filled with non-zero entries) | 0 … 1 | 0 | 0 | 0 |  | J+68 | HzCtl_Hi5Lim ♬ | Frequency limit for high frequency de- coupling protection (f5>) in Hz | s. Technical Infor- mation sheet | 58 | 54 | 58
J+68 | PPltCtlGain | Active power pilot control gain (see block diagram in the appendix; set to 0 for disabling this function) | 0 … tbd | 0 |  | 0 |  | J+69 | HzCtl_Hi5LimTm ♬ | Delay for high frequency decoupling protection (f5>) in s | s. Technical Infor- mation sheet | 0.01 | 0.08 | 0.01
J+69 | QPltCtlGain | Reactive power pilot control gain (see block diagram in the appendix; set to 0 for disabling this function) | 0 … tbd | 0 |  | 0 |  | J+70 | HzCtl_Hi4Lim ♬ | Frequency limit for high frequency de- coupling protection (f4>) in Hz | s. Technical Infor- mation sheet | 57 | 53 | 57
J+70 | QV_QSXArr_0 | Q(V) control characteristics x0 | 0 … 2 | 0.8 |  | 0.8 |  | J+71 | HzCtl_Hi4LimTm ♬ | Delay for high frequency decoupling protection (f4>) in s | s. Technical Infor- mation sheet | 0.01 | 0.09 | 0.01
J+71 | QV_QSXArr_1 | Q(V) control characteristics x1 | 0 … 2 | 0.9 |  | 0.9 |  | J+72 | HzCtl_Hi3Lim ♬ | Frequency limit for high frequency de- coupling protection (f3>) in Hz | s. Technical Infor- mation sheet | 56 | 53 | 56
J+72 | QV_QSXArr_2 | Q(V) control characteristics x2 | 0 … 2 | 0.95 |  | 0.95 |  | J+73 | HzCtl_Hi3LimTm ♬ | Delay for high frequency decoupling protection (f3>) in s | s. Technical Infor- mation sheet | 0.01 | 10 | 0.01
J+73 | QV_QSXArr_3 | Q(V) control characteristics x3 | 0 … 2 | 0.99 |  | 0.99 |  | J+74 | HzCtl_Hi2im ♬ | Frequency limit for high frequency de- coupling protection (f2>) in Hz | s. Technical Infor- mation sheet | 55 | 52 | 55
J+74 | QV_QSXArr_4 | Q(V) control characteristics x4 | 0 … 2 | 1.01 |  | 1.01 |  | J+75 | HzCtl_Hi2LimTm ♬ | Delay for high frequency decoupling protection (f2>) in s | s. Technical Infor- mation sheet | 0.01 | 150 | 0.01
J+75 | QV_QSXArr_5 | Q(V) control characteristics x5 | 0 … 2 | 1.05 |  | 1.05 |  | J+76 | HzCtl_Hi1Lim ♬ | Frequency limit for high frequency de- coupling protection (f1>) in Hz | s. Technical Infor- mation sheet | 53 | 51 | 53
J+76 | QV_QSXArr_6 | Q(V) control characteristics x6 | 0 … 2 | 1.1 |  | 1.1 |  | J+77 | HzCtl_Hi1LimTm ♬ | Delay for high frequency decoupling protection (f1>) in s | s. Technical Infor- mation sheet | 60 | 800 | 60
J+77 | QV_QSXArr_7 | Q(V) control characteristics x7 | 0 … 2 | 1.2 |  | 1.2 |  | J+78 | HzCtl_Lo1Lim ♬ | Frequency limit for low frequency de- coupling protection (f1<) in Hz | s. Technical Infor- mation sheet | 47 | 49 | 47
J+78 | QV_QSYArr_0 | Q(V) control characteristics y0 | 0 … 1 | 0.5 |  | 0.5 |  | J+79 | HzCtl_Lo1LimTm ♬ | Delay for low frequency decoupling protection (f1<) in s | s. Technical Infor- mation sheet | 60 | 800 | 60
J+79 | QV_QSYArr_1 | Q(V) control characteristics y1 | 0 … 1 | 0.4 |  | 0.4 |  | J+80 | HzCtl_Lo2Lim ♬ | Frequency limit for low frequency de- coupling protection (f2<) in Hz | s. Technical Infor- mation sheet | 45 | 48 | 45
J+80 | QV_QSYArr_2 | Q(V) control characteristics y2 | 0 … 1 | 0.2 |  | 0.2 |  | J+81 | HzCtl_Lo2LimTm ♬ | Delay for low frequency decoupling protection (f2<) in s | s. Technical Infor- mation sheet | 0.01 | 150 | 0.01
J+81 | QV_QSYArr_3 | Q(V) control characteristics y3 | 0 … 1 | 0 |  | 0 |  | J+82 | HzCtl_Lo3Lim ♬ | Frequency limit for low frequency de- coupling protection (f3<) in Hz | s. Technical Infor- mation sheet | 44 | 46.5 | 44
J+82 | QV_QSYArr_4 | Q(V) control characteristics y4 | 0 … -1 | 0 |  | 0 |  | J+83 | HzCtl_Lo3LimTm ♬ | Delay for low frequency decoupling protection (f3<) in s | s. Technical Infor- mation sheet | 0.01 | 10 | 0.01
J+83 | QV_QSYArr_5 | Q(V) control characteristics y5 | 0 … -1 | -0.3 |  | -0.3 |  | J+84 | HzCtl_Lo4Lim ♬ | Frequency limit for low frequency de- coupling protection (f4<) in Hz | s. Technical Infor- mation sheet | 43 | 46 | 43
J+84 | QV_QSYArr_6 | Q(V) control characteristics y6 | 0 … -1 | -0.5 |  | -0.5 |  | J+85 | HzCtl_Lo4LimTm ♬ | Delay for low frequency decoupling protection (f4<) in s | s. Technical Infor- mation sheet | 0.01 | 0.09 | 0.01
J+85 | QV_QSYArr_7 | Q(V) control characteristics y7 | 0 … -1 | -0.6 |  | -0.6 |  | J+86 | HzCtl_Lo5im ♬ | Frequency limit for low frequency de- coupling protection (f5<) in Hz | s. Technical Infor- mation sheet | 42 | 45 | 42
J+86 | QLimNeg | Negative reactive power limit in p.u. | 0 … -1.0 | -0.55 |  | -0.422 |  | J+87 | HzCtl_Lo5LimTm ♬ | Delay for low frequency decoupling protection (f5<) in s | s. Technical Infor- mation sheet | 0.01 | 0.08 | 0.01
J+87 | QLimPos | Positive reactive power limit in p.u. | 0 … 1.0 | 0.55 |  | 0.422 |  | J+88 | HzCtl_Lo6Lim ♬ | Frequency limit for low frequency de- coupling protection (f6<>) in Hz | s. Technical Infor- mation sheet | 41 | 44 | 41
J+88 | VDroopQLimNeg | Voltage droop characteristics: nega- tive reactive power limit in p.u. | 0 … -1.0 | -0.4 |  | -0.422 |  | J+89 | HzCtl_Lo6LimTm ♬ | Delay for low frequency decoupling protection (f16<) in s | s. Technical Infor- mation sheet | 0.01 | 0.05 | 0.01
J+89 | VDroopQLimPos | Voltage droop characteristics: positive reactive power limit in p.u. | 0 … 1.0 | 0.4 |  | 0.422 |  | J+90 | KPLL1 ♬ | First-order low-pass filter time delay (valid for PLLFlag = 0) |  | 30 | 30 | 30
[8 empty] | J+91 | PLLFlag ♬ | Determines whether inverter PLL is modeled by a simple first-order delay (0) with parameter KPLL1, or by a PLL control loop (1) with parameters KPPLL2 and KIPLL2. For experimental studies the PLL can also be disabled: PLLFlag = 2: angle is directly obtained from PSS®E BUSDAT routine PLLFlag = 3: angle is directly obtained from measurement of the complex bus voltage VOLT(IB) | 0 … 3 | 1 | 1 | 1
[8 empty] | J+92 | KPPLL2 ♬ | PLL 2 control loop control gain (valid for PLLFlag = 1) |  | 10 | 10 | 10
ICON | Parameter | Description | Range | Default |  | Griffith |  | J+93 | KIPLL2 ♬ | PLL 2 control loop integration gain (valid for PLLFlag = 1) |  | 30 | 30 | 30
M | Rbus | Bus number of the remotely regulated bus; “from” bus | n/a | n/a |  |  |  | J+94 | HzFltTm ♬ | Time constant of first-order lag fre- quency filter; if this parameter is > 0 then the frequency is determined by filtering the system frequency (1.0 + BSFREQ(IB))*f) with this filter, where f = 50 or 60. This parameter is overwritten by PLLFlag2. | 0 … 10 | 0 | 0 | 0
M+1 | ToBus | Bus number of the “to” bus assigned to the remotely regulated bus; The Power Plant Controller controls the power flowing from the “from” bus to the “to” bus | n/a | n/a |  |  |  | J+95 | PLLFlag2 ♬ | Activation of second PLL model for fre- quency measurement | 0: deactivated 1: activated | 0 | 0 | 0
M+2 | CID | Circuit id for power measurement rou- tine FLOW | n/a | -1 |  |  |  | J+96 | KPPLL3 ♬ | PLL 2 control loop control gain (valid for PLLFlag2 = 1) |  | 5 | 5 | 5
M+3 | Switch | Switch for power measurement rou- tine FLOW | n/a | 0 |  |  |  | J+97 | KIPLL3 ♬ | PLL 2 control loop integration gain (valid for PLLFlag2 = 1) |  | 0.3 | 0.3 | 0.3
M+4 … M+53 | GenBusNums | Bus numbers of generators with SMASC model C1.35 and later ver- sions; set to zero if only one genera- tor is controlled | n/a | n/a |  |  |  | J+98 | Reserved | Should be set to 0. If set to values greater than 0, this parameter defines the number of a signal debug text file (see CON(J+99), too). |  | 0 | 0 | 0
[8 empty] | J+99 | Reserved ♬ | If set to values greater than 0, some model information is logged when the model is called by PSS®E; if set 0, this is suppressed. At the same time, this parameter specifies the time span |  | 1 | 0 | 1
[8 empty] | J+100 | GenTrpFlag ♬ | Determines whether the generator is tripped through the GENTRP com- mand (1) or not (0). If GENTRPFLAG = 0, then only the current injection commands for direct and quadrature current are set to zero, but the generator is not tripped using GENTRP. If GENTRPFLAG = 1, then the genera- tor is tripped using GENTRP. | 0: deactivated 1: activated | 1 | 1 | 1
[8 empty] | J+101 | PPrioEna ♬ | Activation of active power priority switch | 0: deactivated 1: activated | 0 | 0 | 0
101 'USRMDL' 1 'SMAPPC121' 4 0 54 120 20 70 106 107 -1 1 | [7 empty] | J+102 | SMASCSFlag ♬ | Activation of storage inverter function- ality; set to 1 for simulation of storage inverters; set to 2 for simulation of combined PV/storage setup | 0: deactivated 1: storage-only 2: PV/storage | 0 | 0 | 0
0 0 0 0 0 0 0 0 0 0 | [7 empty] | J+103 | DischargeTm ♬ | Battery discharge time in s; see sec- tion 4.8. | 0 … tbd | 9999 | 360 | 9999
0 0 0 0 0 0 0 0 0 0 | [7 empty] | J+104 | SOCIni ♬ | Battery state of charge at initialization in p.u. | 0 … 1 | 0.7 | 0.5 | 0.7
0 0 0 0 0 0 0 0 0 0 |  |  |  |  | ` |  |  | J+105 | KP_C ♬ | Charge PI controller proportional gain | 0 … tbd | 0.01 | 0.01 | 0.01
0 0 0 0 0 0 0 0 0 0 | [7 empty] | J+106 | KI_C ♬ | Charge PI controller integral gain | 0 … tbd | 0.001 | 0.05 | 0.001
0 0 0 0 0 0 0 0 0 0 | [7 empty] | J+107 | CDB ♬ | Charge controller deadband | 0 … 1 | 0 | 0 | 0
2 | [7 empty] | J+108 | CNom ♬ | Charge controller set-point | 0 … 1 | 0.7 | 0.5 | 0.7
0 1 0.03 0 | [7 empty] | J+109 | FSCScale ♬ | Scaling of charge pilot control signal | tbd | 1 | 1 | 1
0 0.5 0.02 0.01 | [7 empty] | J+110 | ChargePMax ♬ | Maximum charge power of the stor- age inverter | 0 … 1 | 1 | 1 | 1
0.9123 1 0 0.035 0.0938 |  |  |  |  | ` |  |  | J+111 | ChargePMin ♬ | Minimum charge power of the stor- age inverter | 0 … 1 | 1 | 1 | 1
0 0.5 0.03 0 0.9 | [7 empty] | J+112 | SMASCONI ♬ | If set to zero, writing into the file SMASCONi.txt is suppressed (only for multiple generator support). | 0 … 1 | 0 | 0 | 0
0.04 0.04 -0.6 0.6 | [7 empty] | J+113 | QVArScale ♬ | Multiplication factor for Iq set-point signal for plant control response time correction. | tbd | 1 | 0.6 | 1
0.88 0.88 1.12 1.12 0 0.1 | [7 empty] | J+114 | Reserved | n/a | n/a | n/a | 0 | n/a
1 0.5 0.03 0 1 | [7 empty] | J+115 | Reserved | n/a | n/a | n/a | 0 | n/a
0 0 | [7 empty] | J+116 | Reserved | n/a | n/a | n/a | 0 | n/a
0 0.2 0.05 0.4 0.01 0 | [7 empty] | J+117 | Reserved | n/a | n/a | n/a | 0 | n/a
1 1 0 | [7 empty] | J+118 | Reserved | n/a | n/a | n/a | 0 | n/a
47 48 49.7 49.85 50.15 51 52 52.65 | [7 empty] | J+119 | Reserved | n/a | n/a | n/a | 0 | n/a
0.05 0.05 0.05 0 0 -0.3043 -0.6623 -1
0 0.01 0.01 0 1 1
0
0 0
0.8 0.9 0.95 0.99 1.01 1.05 1.1 1.2
0.5 0.4 0.2 0 0 -0.3 -0.5 -0.6
-0.422 0.422
-0.422 0.422
0.0 0.0 0.0 0.0 0.0 0.0
0.0 0.0 0.0 0.0 0.0 0.0 0.0 0.0
0.0 0.0 0.0 0.0 0.0 0.0 0.0 0.0
0.0 0.0 0.0 0.0 0.0 0.0 0.0 0.0/
101 'USRMDL' 1 'SMASC146' 1 1 0 120 40 200
1 1 0 0.9 0.9 0 1 0 0.3
1 0.01 14.066 0.422 60
0 0.9 0.5 1 0.9 0.9
0 0.2 0.05 0.5
0.26 1
2 4 2 4
0.13 0.13 0.13 0.13 0.03 0.05
0.01 0 0.01 0.1 100 0 0
0 0.125 0.1
1.5 0.01 1.5 0.01 1.45 0.5 1.3 1 1.2 30
0.85 30 0.75 20 0.4 2 0.3 2 0.1 1.5
59 0.01 58 0.01 57 0.01 56 0.01 55 0.01 53 60
47 60 45 0.01 44 0.01 43 0.01 42 0.01 41 0.01
30 1 10 30 0 0 5 0.3
0 1 1 0
0 9999 0.7 0.01 0.001 0 0.7 1
1 1
0 1
0.0 0.0 0.0 0.0 0.0 0.0/